## Pinouts
| Arduino MEGA | https://store.arduino.cc/usa/mega-2560-r3 |  | *Requirements are: | Ethernet shield + SD card
| Ethernet Shield | https://store.arduino.cc/usa/arduino-ethernet-shield-2 |  |  | 1 x CO2 + 3 x Hum
| Arduino 4 relays Shield | https://store.arduino.cc/usa/4-relays-shield |  |  | 1 x DS18B20
| DF Robot 4 relays Shield | https://abra-electronics.com/electromechanical/relays/relay-modules-shields/dfr0144-relay-shield-for-arduino-dfr0144.html |  |  | 1 x porte
3 x Beignes de courant
|  | NUS = Not used by shield |  |  | 3 x pompes (relay shield)
Deprecated
Pins | Description (MEGA) | Ethernet Shield | DFR0144 | All together* |  | 4 Relays Shield (connects with MEGA)
Left side
- | - |  | NUS | Cannot use (ethernet shield does not have a full header) |  | NUS
IOREF |  |  | NUS | Cannot use (ethernet shield does not have a full header) |  | Used for Schottky diode protection on A2 and A3
RESET | Reset | Reset (connects to ICSP header too) | RESET (xbee) and reset button | Reset |  | To reset button
3.3V |  | 3V3 - But there is also two LDO | NUS | Power |  | NUS
5V |  | 5V | NUS | Power |  | 5V
GND |  | GND | GND | Power |  | GND
GND |  | GND | GND | Power |  | GND
Vin |  | NUS | Vin (with a diode) | Power |  | NUS
A0 |  | WP - 10k pull up - For a regular SD card socket | A0 (goes to header) | Do not use |  | NUS
A1 |  | Detect - 10k pull up - idem | A1 (goes to header) | Do not use |  | NUS
A2 |  | NUS | A2 (goes to header) | Spare |  | Header A2
A3 |  | NUS | A3 (goes to header) | Spare |  | Header A3
A4 |  | NUS | A4 (goes to header) | Spare |  | NUS
A5 |  | NUS | A5 (goes to header) | Spare |  | NUS
A6 |  |  |  | Spare
A7 |  |  |  | Spare
A8 |  |  |  | Spare
A9 |  |  |  | Spare
A10 |  |  |  | Spare
A11 |  |  |  | Spare
A12 |  |  |  | Spare
A13 |  |  |  | Spare
A14 |  |  |  | Spare
A15 |  |  |  | Spare
Right Side
SCL | SCL (TWI) |  | SCL (goes to header) | Cannot use (ethernet shield does not have a full header) |  | TWI header (x2)
SDA | SDA (TWI) |  | SDA (goes to header) | Cannot use (ethernet shield does not have a full header) |  | TWI header (x2)
AREF |  | NUS | NUS | Spare |  | NUS
GND |  | GND | GND | Power |  | GND
D13 | Built-in LED / PWM | D13 (goes to a LED) | D13 (goes to header) | Built-in led |  | NUS
D12 | PWM | NUS | D12 (goes to header) | Spare |  | Controls relay 4 + has 10k pulldown
D11 | PWM | NUS | D11 (goes to header) | Spare |  | NUS
D10 | PWM | Slave Select (SS) | Controls relay 4 / Through a jumper | Ethernet | Will need to remove the jumper | NUS
D9 | PWM | NUS | D9 (goes to header) | Spare |  | NUS
D8 | PWM | NUS | Controls relay 3 / Through a jumper | Pompe 3 |  | Controls relay 3 + has 10k pulldown
D7 | PWM | NUS | Controls relay 2 / Through a jumper | Pompe 2 |  | Controls relay 2 + has 10k pulldown
D6 | PWM | NUS | D6 (goes to header) | Spare |  | Header out6
D5 | PWM | NUS | D5 (goes to header) | Spare |  | Header out5
D4 | PWM | SD chip select | D4 (goes to header) | SD chip select |  | Controls relay 1 + has 10k pulldown
D3 | PWM | NUS | D3 (goes to header) | Spare |  | NUS
D2 | PWM / Interrupt 1 | PD2 - Jumper not soldered - interrupt | Controls relay 1 / Through a jumper | Pompe 1 | Was not working with DS18B20 (MEGA + Ethernet shield). | NUS
D1 | TX0 (UART) | NUS | D1 (goes to header) / has a 15k pull down | Spare |  | NUS
D0 | RX0 (UART) / Interrupt 0 | NUS | D0 (goes to header) / goes to switch to reset xbee | Spare |  | NUS
D14 | TX3 (UART) |  |  | Spare
D15 | RX3 (UART) |  |  | Spare
D16 | TX2 (UART) |  |  | Spare
D17 | RX2 (UART) |  |  | Spare
D18 | TX1 (UART) / Interrupt 5 |  |  | Spare
D19 | RX1 (UART) / Interrupt 4 |  |  | Spare
D20 | SDA (TWI) / Interrupt 3 |  |  | 1 x CO2 + 3 x Hum (I2C) + TCA9548A
D21 | SCL (TWI) / Interrupt 2 |  |  | 1 x CO2 + 3 x Hum (I2C) + TCA9548A
ICSP Header (for uC)
1 | MISO | MISO |  | SD card + Ethernet |  | (no ICSP header)
2 | VCC | VCC |  | Power
3 | SCK | SCK |  | SD card + Ethernet
4 | MOSI | MOSI |  | SD card + Ethernet
5 | RESET (inverted logic) | RESET |  | SD card + Ethernet
6 | GND | GND |  | Power
Bottom (upper row)
GND |  |  |  | Power
D52 | SCK | Do not use |  | SD card + Ethernet
D50 | MISO | Do not use |  | SD card + Ethernet
D48 |  |  |  | Spare
D46 | PWM |  |  | Spare
D44 | PWM |  |  | Spare
D42 |  |  |  | Spare
D40 |  |  |  | Spare
D38 |  |  |  | Spare
D36 |  |  |  | Spare
D34 |  |  |  | Spare
D32 |  |  |  | Spare
D30 |  |  |  | Door sensor
D28 |  |  |  | Spare
D26 |  |  |  | Spare
D24 |  |  |  | Spare
D22 |  |  |  | Spare
5V |  |  |  | Power
Bottom (lower row)
GND |  |  |  | Power
D53 | SS | Need to be set to output! |  | SD card + Ethernet
D51 | MOSI | Do not use |  | SD card + Ethernet
D49 |  |  |  | Spare
D47 |  |  |  | Spare
D45 | PWM |  |  | Spare
D43 |  |  |  | Spare
D41 |  |  |  | Spare
D39 |  |  |  | Spare
D37 |  |  |  | DS18B20
D35 |  |  |  | Spare
D33 |  |  |  | Spare
D31 |  |  |  | Spare
D29 |  |  |  | Spare
D27 |  |  |  | Spare
D25 |  |  |  | Spare
D23 |  |  |  | Spare
5V |  |  |  | Spare

## Arduino_Mega_Specs
Arduino MEGA
6 interrupts | Pin
interrupt 0 | 0
interrupt 1 | 3
interrupt 2 | 21
interrupt 3 | 20
interrupt 4 | 19
interrupt 5 | 18
Multi-tasking is available but not supported by Arduino IDE
Need to use another software such as FreeRTOS or RTX
Pins Arduino Mega | Pin description
from: https://www.theengineeringprojects.com/2018/06/introduction-to-arduino-mega-2560.html
D0 - D53 | 54 digital input / output pins.
A0 - A15 | 16 Analog input / output pins.
D2 - D13 | 12 Pulse Width Modulation ( PWM ) pins.
Pin #0 (RX), pin #1 (TX) Pin #19 (RX1), pin #18 (TX1) Pin #17 (RX2), pin #16 (TX2) Pin #15 (RX3), pin #14 (TX3) | 4 serial communication ports (8 pins).
Pin #50 ( MISO ) Pin #51 ( MOSI ) Pin #52 ( SCK ) Pin #53 ( SS ) | SPI Communication pins.
Pin #20 ( SDA ), Pin #21 ( SCL ) | I2C Communication pins.
Pin #13 | Built-in LED for testing.

## Power Consumption_Est
Power consumption estimation:
Arduino MEGA | 20mA per digital pins | 200mA max for the chip
Relay board | 35 mA per coil on. | 140mA
Ethernet shield | 5mA for W5500
BME280 | 3mA
K30 | 40mA
DS18B20 | 1.5mA
T6713 | 200mA peak, 25mA average
LD1117 can provide up to 800mA

## Unit_tests_MEGA
| Board: | " Arduino / Genuino Mega or Mega 2560 "
| Processor: | " ATmega2560 (Mega 2560)"
| Port: | " COM8 (Arduino / Genuino Mega or Mega 2560)"
| Programmer: | "ArduinoISP"
Test Nb | Description | Hardware | Script used | Pass / Fail | Comments | static Memory (bytes / percent) | Dynamic Memory (bytes / percent) | Library (ies) used
1 | Basic Blink LED test | MEGA | 01_blink | Pass | See the led blink | 1448 (0%) | 9 (0%) | None
2 | Basic SD file create write read delete | MEGA + Ethernet shield | 02_SD_card_basic_test | Pass | File gets created, written, read, and deleted | 12160 (4%) | 1134 (13%) | SPI, SD
3 | Basic Ethernet webserver | MEGA + Ethernet shield | 03_Ethernet_web_server | Pass | See the Analog input 0 to 5 on Firefox (192.168.11.177:80) refreshes every few seconds. Values are between 330 and 390 (nothing is connected on the Aout). Direct connection between ethernet shield and computel. Laptop is 192.168.11.155 | 12658 (4%) | 769 (9%) | SPI, Ethernet
4 | Basic Ethernet + SD Card | MEGA + Ethernet shield | 04_sd_files_over_ethernet | Pass | I can connect to the ethernet shield through Firefox and download the file test.txt Direct connection between ethernet shield and computel. Laptop is 192.168.11.155 | 22238 (8%) | 1395 (17%) | SPI, SD, Ethernet
5 | Basic 2 x DS18B20 temp reading | MEGA + 2 DS18B20 + 4k7 | 05_multiple_DS18B20 | Pass | Requesting temperatures...DONE Device Address: 28AACC44401401D8 Temp C: 18.37 Temp F: 65.07 Device Address: 28AA393440140104 Temp C: 20.25 Temp F: 68.45 | 7008 (2%) | 584 (7%) | OneWire, DallasTemperature
6 | Basic 1 SHT30-D humidity reading | MEGA + 1 SHT30-D | 06_single_SHT30-D_auto_detect | Pass | Serial monitor, see the RH and the temperature refreshing every few seconds. No external pull-ups are connected to the I2C SDA and SCL | 7452 (2%) | 544 (6%) | Wire, SHTSensor (arduino-sht) | https://github.com/Sensirion/arduino-sht
7 | Basic 1 T6713 CO2 reading | MEGA + 1 T6713 | 07_co2_sensor_T6713 | Pass | Following Application Note AN161. The CO2 measurement was refreshing every 2s. Roughly 1100 ppm. Increased when I started to breathe closer to the sensor. No custom library required. | 4480 (4%) | 502 (6%) | Wire
8 | Basic current measurement 1 | MEGA + 1 SCT013 | 08_current_measurement_SCT013 | Failed | See the current varying when I change the speed of the fan (about 0.15 to 0.18 A). It is working properly, however: The SCT013 is for AC Current only! Cannot use it with the NMP30 motor (12V dc) | 4354 (1%) | 316 (3%) | EmonLib
9 | Basic current measurement 2 | MEGA + INA219 | 09_current_measurement_INA219 | Pass | There is another library called ArduinoINA219 that seems more complete. Kept the default range 32V - 2 Amps in case all three motors runs at the same time. When the INA219 is not connected, it still output some values (not good). When there is no load, we see see about 1mA. Since our INA219 is right before the ground, we can't use the bus voltage function. Need to update to put it on the plus side. | 6500 (2%) | 573 (3%) | Wire, Adafruit_INA219
10 | Basic door sensor | MEGA + door sensor |  | To do | Need to select the door sensor
11 | Multiple I2C devices | MEGA + T6713 + SHT30-D | 11_multiple_I2C_sht30_and_T6713 | Failed | We see the CO2 measure, temp and RH but: We cannot change the I2C address of the SHT30-D because it is packaged. Therefore we need an I2C multiplexer to have more than one humidity sensor | 7946 (3%) | 652 (7%) | Wire, SHTSensor (arduino-sht) | https://www.adafruit.com/product/2717?gclid=Cj0KCQiAno_uBRC1ARIsAB496IXwtkuNF7uFfyh3HG0cQmPJ2nLFbEd4LbUi5byNprLV6e8FQdiS5lEaAi-CEALw_wcB
12 | Multiple devices + SD card + ethernet | MEGA + Ethernet + DS18B20 + SHT30-D | 12_integration_sd_ethernet_ds18b20_sht30 | Pass | The two ds18b20 and the sht30 writes properly to the SD file. The file can be transferred from the Firefox browser. The laptop IP address is 192.168.11.155 The web browser is quite slow because I am using a delay in the script. 30K is required for the static memory. Uno is 31.5K. All the files' names are in capitals. I don't know why. | 30882 (12%) | 2190 (26%) | Wire, DallasTemperature, Wire, SHTSensor, SPI, SD, Ethernet | https://abra-electronics.com/robotics-embedded-electronics/breakout-boards/level-shifters-and-expanders/2717-ada-tca9548a-i2c-multiplexer.html
13 | Basic relay control | MEGA + DFR0144 | 13_basic_relay_control_DFR0144 | Pass | Relay pins = 2, 7, 8, 10. Specs in the datasheet are only for resistive loads. Need to use the external power (the jack). | 2966 (1%) | 296(3%) | None
14 | Basic Motor control | MEGA + DFR0144 + NMP30 | 14_basic_relay_and_motor_control_DFR0144 | Pass | Added a 1N4004 in parallel to the motor. Motor starts and stops properly. Same script as test number 13 I noticed the relays were hot after a while (seems correct). | 2966 (1%) | 296(3%) | None
15 | Basic relay/Motor + current measurement | MEGA + DFR0144 + NMP30 + INA219 | 15_one_pump_and_current_measurement_INA219 | Pass | The measurement seems to be working fine in terms of power. Need to make another test that reads as often as possible to try to catch the inrush current. Need to add capacitors for the inrush current The results are way lower than the motor specs. (we get 500mW but the motor is rated 12V/0.46Amps, so it should be up to 5W). Should we add an RC at the input of the chip? | 6778 (2%) | 601 (7%) | Wire, Adafruit_INA219
16 | Multiple I2C devices with multiplexer | MEGA + 2 SHT30 + TCA9548A | 16_basic_I2C_multiplexer_TCA9548A | Pass | Works as expected. The reset should have a pull-up to Vcc I don't know why but for each SHT30 sensor, there are two I2C addresses displayed (0x0 and 0x44) | 4210 (1%) | 446(5%) | Wire, utility/twi.h
17 | Sensors Temp. comparison | MEGA + DS18B20 + SHT30 | 17_temp_comparison_ds18b20_sht30 | Pass | The error between two ds18b20 is bigger than the error between a ds18b20 and an SHT30. It gives roughly an error of 2% | 10776 (4%) | 932 (11%) | OneWire, DallasTemperature, Wire, SHTSensor
18 | Three shields together | MEGA + Ethernet + DFR0144 | 18_three_shields_together | Pass | I had to unsolder the servo connector and one of the pins from the I2C header. The shields still do not fit perfectly but it works. I added spacers between the ethernet shield and the arduino so that it does not move when pressing on the relays shield. Added electrical tape on the RJ45 to avoid shorts. Will need to change the headers (at least 12mm) + add standoffs SD card not easily accessible. Need an extender There is one pin conflict: cannot use relay 4. Removed the jumper. The relays toggle every second. Can fetch the file on internet properly. SD card and ethernet were properly started. When dowloading a file, sometimes we can see the relay takes more than one second to toggle again. Disconnecting and reconnecting the ethernet cable does not seem to have an impact. | 22398 (8%) | 1401 (17%) | SPI, SD, Ethernet | https://abra-electronics.com/interconnects/connectors/headers/female/prt-11417-arduino-stackable-header-kit-r3-prt-11417.html
19 | Three motors at the same time | MEGA + DFR0144 + 3 NMP30 | 19_three_motors_with_relays | Pass | Everything is working as expected. We will need to fix the motors quite well because they are moving quite a bit. No fluctuation seen in the LED | 2706 (1%) | 188 (2%) | None
20 | Three motors + current measurement | MEGA + DFR0144 + 3 NMP30 + INA219 | 20_three_motors_with_current_measurement_INA219 | Pass | We can see a voltage drop when more than one motor is activated. We can see current spikes of 1.5A (when starting only one motor). In steady states all three motors requires only 800mA total. Need to add capacitors! It is not that obvious that all motors are on when looking only at the current. Need to wait for steady-state. Added 0.5s of delay after pump ON and before reading measurements and the thread is way easier to analyze. | 7096 (2%) | 679 (8%) | Adafruit_INA219
21 | All the sensors together + Ethernet + SD | MEGA + ethernet shield + 2 DS18B20 + 2 SHT30 + INA219 + T6713 | 21_all_sensors_with_ethernet_and_sd | Pass | Everything is working as expected. Not sure about the format in the file, to discuss with Marc. CO2 sensor reading seems to be quite high. | 34036 (13%) | 2505 (30%) | OneWire, DallasTemperature, Wire, SHTSensor, SPI, SD, Ethernet, Adafruit_INA219
22 | Pumps and sensors | MEGA + ethernet shield + 2 DS18B20 + 2 SHT30 + INA219 + T6713 + 3 NMP30 + DFR0144 | 22_all_sensors_and_pumps_with_ethernet_and_sd | Pass | Also working as expected. Implemented a logic for the pumps based on Marc's constants It will not be possible to retrieve files when pumps are working. | 36872 (14%) | 2765 (33%) | OneWire, DallasTemperature, Wire, SHTSensor, SPI, SD, Ethernet, Adafruit_INA219
23 | Remotely fetch the files | MEGA + Ethernet + T6713 + SHT30-D |  | To do | Review what we did for the microgreen setup
24 | Reliability test 1 | MEGA + Ethernet |  | To do | What if power outage when SD file is opened? Simple script opening a file and continuously writing to it.
25 | Basic NTP time stamps | MEGA + Ethernet | 25_Basic_NTP_time_stamps | Pass | It is possible to get the time from internet but it requires DHCP Ethernet.localIP gives the assigned IP. Was able to ping the IP from my computer. Need to figure out to find the IP address without the serial monitor. | 13496 (5%) | 876 (10%) | SPI, Ethernet, EthernetUdp
26 | Display values on internet | MEGA + Ethernet | 26b_thingspeak_multiple_feeds_ethernet_board | Pass | I had to create a new account for ThingSpeak. Limited to 8 fields / update every 20seconds. | 23732 (9%) | 1342 (16%) | ThingSpeak, Ethernet
27 | ThingSpeak + NTP | MEGA + Ethernet | 27_thingspeak_and_NTP | Failed | Combining NTP + Thingspeak I don't know why, I had to cycle the power to make it work. Losing the connections after a few minutes. Had to add Ethernet.maintain() + change MAC address Still losing connection to thingspeak after about 10 mins Maybe it is because of the delays? (most likely, see test 29) | 24900 (9%) | 1489 (18%) | ThingSpeak, Ethernet, SPI, EthernetUdp
28 | ThingSpeak + web server | MEGA + Ethernet | 28_thingspeak_NTP_and_SD | Pass | Seems to be working fine. Script ran for > 10 minutes and it is still working fine | 34642 (13%) | 2308 (28%) | ThingSpeak, Ethernet, SPI, SD
29 | ThingSpeak + web server + NTP | MEGA + Ethernet | 29_thingspeak_webserver_and_NTP | Pass | After 1h15min, still seems to be working fine. Most likely the problem of test 27 was the delays. | 35752 (14%) | 2459 (30%) | ThingSpeak, Ethernet, SPI, EthernetUdp, SD
30 | Maximum length of door sensor | MEGA + 375 |  | To do | Need to test at least 30 feet
31 | Get external IP address | MEGA + Ethernet |  | To do | Need to send external IP to thingspeak.
32 | Basic SD card extender test | MEGA + Ethernet + SD card extender |  | Hardware missing | To make sure it works
33 | Everything together | MEGA + ethernet shield + 2 DS18B20 + 2 SHT30 + INA219 + T6713 + 3 NMP30 + DRF0144 + NTP + AdafruitIO |  | To do | Need to be careful about the delays! We might loose internet connection. | 45958 (18%) | 3755 (45%) | ThingSpeak, Ethernet, SPI, SD, EthernetUdp, OneWire, DallasTemperature, Wire, SHTSensor, AdafruitINA219
34 | Reliability test 2 | MEGA + Ethernet |  | To do | What if we lose internet connection?

## Bills_of_Materials_v2
Old bill of materials at the end of the sheet
Bills of Materials | [6 empty] | *Requirements are: | Ethernet shield + SD card
Components | MFG P/N | Qte | Got it? | Dimensions |  | Comment |  | 1 x CO2 + 3 x Hum
1 x DS18B20
Shields | [7 empty] | 1 x porte
Arduino Mega 2560 |  | 1 | Yes |  |  |  |  | 3 x Beignes de courant
Ethernet Shield |  | 1 | Yes |  |  |  |  | 3 x pompes (relay shield)
DFR0144 |  | 1 | Yes | 95x65mm
Multiplexer I2C | TCA9548A | 1 | No | 30.6mm x 17.6mm x 2.7mm |  | https://www.digikey.ca/product-detail/en/adafruit-industries-llc/2717/1528-1363-ND/5604376
Sensors
Humidity | SHT30-D | 2 | Yes |  |  | Only two needed for mycotrophe
Temperature | DS18B20 | 3 | Yes
Porte | ADA375 | 1 | No |  |  | https://www.digikey.ca/product-detail/en/375/1528-1907-ND/6691113/?itemSeq=313684128
CO2 | T6713 | 1 | Yes
Mesure de courant | INA219 | 3 | No | 22.86 x 20.32 mm |  | https://www.digikey.ca/product-detail/en/904/1528-1168-ND/5353628/?itemSeq=313682087
Connectors
Jack-plug RJ45 |  | 1 | No |  |  | https://www.digikey.ca/product-detail/en/RCP-5SPFFH-SCM7001/1754-1125-ND/7102729/?itemSeq=313680556
DC jack connector - chassis mount |  | 2 | No | One for 9V and one for 12V |  | https://www.digikey.ca/product-detail/en/tensility-international-corp/54-00151/839-1580-ND/9829987
DC jack connector - male |  | 1 | No |  |  | https://www.digikey.ca/product-detail/en/EP501A/EP501A-ND/2439550/?itemSeq=313682865
Terminal block header - 10 pins |  | 1 | No |  |  | https://www.digikey.ca/product-detail/en/phoenix-contact/0707316/277-6149-ND/348296
Terminal block plug - 10 pins |  | 1 | No |  |  | https://www.digikey.ca/product-detail/en/phoenix-contact/1873731/277-8959-ND/3605537
Terminal block header - 4 pins |  | 2 | No |  |  | https://www.digikey.ca/product-detail/en/phoenix-contact/0707264/277-5988-ND/348293
Terminal block plug - 4 pins |  | 2 | No |  |  | https://www.digikey.ca/product-detail/en/phoenix-contact/1902136/277-14330-ND/2525844
Arduino header |  | 1 | No |  |  | https://www.digikey.ca/product-detail/en/PRT-11417/1568-1413-ND/6161755/?itemSeq=313680580
Power supply 9V |  | 1 | No |  |  | Pourrait être 12V aussi
Power supply 12V |  | 1 | No |  |  | Pour le CO2 box
Pompes | NMP30 | 3 | Yes
boîtier |  | 1 | No |  |  | Marc va le faire au fablab
SD Card extender |  | 1 | No |  |  | 10 cm de long
standoff |  | 2 | No
Passe-fil |  | 1 | No
RC snubber |  |  |  | Not sure if necessary
Led |  | 4 | No
Old bill of materials
| Last update: | 2020-01-03
Bills of Materials
| Components | MFG P/N | Qte | Got it? | Comment
Shields
| Arduino Mega 2560 | 7630049200067 | 1 | No | Marc purchased it (shipped directly to me) but I haven't received it.
| Ethernet Shield 2 | 7630049200364 | 1 | No | No news
| 4 Relays Shield | 7630049200654 | 1 | No | No news
Sensors / motors
| CO2 sensor | T6713-5K | 1 | Yes
| Humidity sensor | SHT30-D | 3 | Partially | 1 out of 3
| Temperature sensor | DS18B20 | 4 | Yes
| Door sensor | TBD | 1 | No | Need to test length
| Current sensor | SCT013 | 3 | Partially | 1 out of 3
| Pump | PM 9332-NMP30 | 3 | Partially | 1 out of 3
Misc.
| Tubes for CO2 sensor | NA | TBD | No
| Cover for CO2 sensor | NA | 1 | No
| USB Cable for CO2 sensor | NA | 1 | No | For debugging purposes
| Header of CO2 sensor | NA | 1 | No
| Box for uC | NA | 1 | Yes | 200 x 120 x 75 mm
| Box for pumps | NA | 1 | No | Need to discuss with Marc about that
| Microphone Cable for current sensor |  | 3 | No | Especially if we need to extent the length of the cable
| Pull up resistor for I2C bus | 4.7k | 2 | Yes
| Power supply 120V AC to 12V |  | 1 | No
| Power supply 120V AC to 5V |  | 1 | No | With a jack for Arduino MEGA
| Pull up resistor for DS12B20 | 4.7k | 1 | Yes
Connectors
NMP30
| Suppression diode |  | 3 | No | For back-emf when opening the relay
| RC snubber |  |  |  | Not sure if necessary
I2C devices
Pull-ups
| Multiplexer |  | 1 | No | https://abra-electronics.com/robotics-embedded-electronics/breakout-boards/level-shifters-and-expanders/2717-ada-tca9548a-i2c-multiplexer.html
| INA219 |  | 3 |  | current sensor
| header arduino |  | 1
| standoff |  | 2
[Not used anymore] SCT013
| Capacitor | 10uF | 3 | No | Need low ESR
| Protection diode for 5.5V |  | 3 | No
| Burden Resistor | 3.5k | 3 | No | Potentiometer to adjust
| R1 / R2 | 10k | 6 | No
| Jack connectors |  | 3 | No

## Results_test19
Busoltage (V) | 12.27 | 12.27 | 12.28 | 12.28 | 12.27 | 12.28 | 12.28 | 12.28 | 11.45 | 11.1 | 11.38 | 11.09 | 11.59 | 11.7 | 1.04
Shuntoltage (mV) | 0.11 | 0.09 | 0.11 | 0.11 | 0.07 | 0.11 | 0.1 | 0.1 | 23.47 | 47.57 | 91.69 | 73.21 | 51.2 | 16.82 | 0.07
Loadoltage (V) | 12.27 | 12.27 | 12.28 | 12.28 | 12.27 | 12.28 | 12.28 | 12.28 | 11.47 | 11.15 | 11.47 | 11.17 | 11.64 | 11.72 | 1.04
Current (mA) | 0.9 | 1506.3 | 1 | 1073.7 | 1.1 | 1588.5 | 1 | 219 | 1434.1 | 808.1 | 822.6 | 853.5 | 331.5 | 1.4 | 0.8
Power (mW) | 14 | 12410 | 10 | 9798 | 14 | 10922 | 14 | 10954 | 14270 | 18128 | 8854 | 5770 | 3850 | 14 | 0
Comment |  | ON pump 0 | OFF pump 0 | ON pump 1 | OFF pump 1 | ON pump 2 | OFF pump 2 | ON pump 0 | ON pump 1 | ON pump 2 | All pumps are ON | OFF pump 0 | OFF pump 1 | OFF pump 2 | All pumps are OFF
Same tests but added a delay(500) after activating a pump and before measuring the current
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
Bus Voltage (V) | 12.28 | 11.64 | 12.27 | 11.67 | 12.27 | 11.78 | 12.28 | 11.62 | 11.29 | 11.53 | 11.3 | 11.6 | 11.89 | 12.28 | 12.28
Shunt Voltage (mV) | 0.13 | 31.15 | 0.08 | 26.2 | 0.09 | 27.73 | 0.09 | 26.22 | 83.28 | 68.8 | 91.48 | 46.78 | 27.27 | 0.1 | 0.11
Load Voltage (V) | 12.28 | 11.67 | 12.27 | 11.69 | 12.27 | 11.81 | 12.28 | 11.65 | 11.37 | 11.6 | 11.39 | 11.64 | 11.92 | 12.28 | 12.28
Current (mA) | 1.1 | 297 | 1 | 373.5 | 1.1 | 387.9 | 1.2 | 340.1 | 842.7 | 763.3 | 946.9 | 648.3 | 148.1 | 1 | 0.9
Power (mW) | 14 | 3500 | 14 | 4120 | 14 | 2264 | 14 | 4018 | 6338 | 7746 | 11348 | 5380 | 2460 | 10 | 14
Comment |  | ON pump 0 | OFF pump 0 | ON pump 1 | OFF pump 1 | ON pump 2 | OFF pump 2 | ON pump 0 | ON pump 1 | ON pump 2 | All pumps are ON | OFF pump 0 | OFF pump 1 | OFF pump 2 | All pumps are OFF